1. **SCOPE OF WORK**

This is an indefinite quantity term contract with no guaranteed volume. The County does not guarantee a minimum or maximum dollar amount (if any) or quantity to be purchased. Quantities given are for evaluation purposes only and not a guaranteed quantity to be purchased.

1. **REQUIRMENTS**

Each product offered and provided shall meet or exceed each of the following requirements:

* 1. All air filters must be manufactured in the United States.
  2. All air filters provided under this contract are to be new, first quality, high efficiency, industrial grade air filters, not economy or home grade air filters.
  3. All filters will be rated MERV 8 or greater as per ASHRAE Standard 52.2.
  4. All filters provided will not be any larger than specified and can be within one quarter (1/4) inch smaller of exact sizes.
  5. Initial resistance of filters will not exceed the following:
     1. One-inch (1”) filters: 0.15 “w.g. at 300 fpm or greater
     2. Two-inch (2”) filters: 0.26 “w.g. at 492 fpm or greater
     3. Four-inch (4”) filters: 0.19 “w.g. at 492 fpm or greater
  6. All air filters will be plainly marked on the frame with the manufacturer’s name, size, and direction of air flow.
  7. Air filters will not be cut down or altered, taped, stapled or otherwise attached together to create the required size and/or thickness.
  8. Examples of air filters that meet the above specifications are Filtration Group Series 400 High Capacity; Flanders Pre Pleat 40 LPD High Capacity; Purolator Defiant Mark 80-D.
  9. Air filters will be ordered on a quarterly basis. Quantities ordered each quarter may vary. The County reserves the right to order at additional times during the year if necessary.
  10. Deliveries will be made in accordance with the terms of Exhibit C - General Terms and Conditions for Lake County Florida, using a smaller truck preferably with a lift gate as the delivery location cannot accommodate a trailer truck.

1. **DELIVERY LOCATION**

Lake County Detention Center (West end of the building)

435 West Alfred Street

Tavares, Florida 32778

1. **CONTACT FOR DELIVERIES**

Ole Olsen, Chief Maintenance Supervisor

Office of Facilities Management

Phone: (352) 516-9612

Email: Ole.Olsen@lakecountyfl.gov