- SCOPE OF SERVICES

To establish a vendor pool to perform the cleaning, flushing, and video recording of storm water drainpipes, box culverts, and water quality units on an as needed basis and in conjunction with the County's needs. Contractors shall be required to temporarily plug and dewater individual storm drain segments for a variety of pipe sizes ranging from twelve (12) inches up to seventy-two (72) inches, inlet boxes, box culverts, and water quality units.  Details for each project will be provided on a Project Order Form issued by the County.  All work projects shall be performed in accordance with industry standards and the Florida Department of Transportation (FDOT) “Standard Specifications for Road and Bridge Construction,”, FDEP Stormwater Regulations, Florida Stormwater, Erosion, and Sediment Control Inspector Manual, MUTCD for traffic control.

The County does not guarantee a minimum or maximum dollar amount to be expended on any contract(s) resulting from this solicitation. Orders may be funded in whole or in part with federal funds and is subject to federal requirements including, but not limited to those set forth in 2 C.F.R. Part 200, Appendix II.  Work performed shall be in strict compliance with the latest codes, standards, and practices and in accordance with Federal, State, and Local laws.

- CONTRACTOR’S RESPONSIBILITIES

Contractor shall:

  - Be licensed and fully competent in all aspects of storm drain system cleaning and related services in a safe manner and on an as needed basis.

    - Employ only skilled, qualified workers.

  - Compliance with Department of Environmental Protection (DEP) guidelines shall be required.

  - Appropriate licensing may include underground contractor license.

  - Designate a project manager that shall speak English and have available communication devices with internet access to ensure proper communication and documentation during operations.

  - Provide all-inclusive quotes to provide 100% turnkey projects to include but not limited to all required labor, material, equipment, inspections, travel time, and a clean project work site.

  - Obtain licenses, permits, and fees (including inspection fees) as required to comply with all laws, ordinances, regulations, and code requirements applicable to complete projects.

  - Be responsible for inspections, penalties, fees, fines, or damages caused as the result of completing projects.

  - Be responsible for supplying the water needed as part of their operations.  The County does not have a water supply.  The Contractor will be required to contact the applicable municipality to obtain water and water meters.

  - Furnish all tools and equipment (water, water meters, vac truck, etc.) to complete projects timely.

  - Clean the storm drainpipe, inlet box, box culvert, or water quality unit so that the drainage capacity is one hundred percent (100%) of the existing capacity.  Cleaning shall be done in a manner so as not to damage the storm drainpipe, inlet boxes, box culvert, water quality unit, or the surrounding area.

  - Be responsible for proper disposal of all debris removed and ensure that the disposal complies with all Federal, State and Local laws and regulations and provide documentation of the disposal from an approved facility with each project invoice.  (F.S. 403.7071, F.S. 403.7071)

  - Provide the County with a schedule of completion, with the work commencing within fourteen (14) days of receipt of the Project Order Form.

  - Consult with the County within twenty-four (24) hours prior to any schedule variance, including when work is interrupted due to weather, breakdowns, etc.

  - Ensure all equipment used on County property is in good, safe working order, and properly maintained to protect the operator and the public. All equipment used by the contractor is subject to inspection by the County.

  - Ensure all moving vehicles are equipped at a minimum with properly operating amber flashing or white strobe lights. All safety devices installed by the manufacturer shall be in place and in proper working order at all times.

- COUNTY RESPONSIBILITIES

County will:

  - Reserve the right to award to one or more vendors.

  - Reserve the right to add or remove services in conjunction with the County’s needs.

  - Reserve the right to inspect and approve all material, supplies, workmanship, and equipment for contract performance.

  - Provide a detailed Project Order Form for each project.

  - Locate and designate all manhole access points for the work, provide right of entry to these points.

  - Reserve the right to dismiss Contractor’s staff for disorderly conduct or unsatisfactory performance in accordance with contract specifications.

- TECHNICAL REQUIREMENTS

  - PLUGGING AND DEWATERING

    - Dewatering plans require county approval prior to work start. The costs will be based on a daily unit price for each pipe size as shown on the bid sheet.

    - When plug installation is required to complete the work the costs shall be based on the size of the pipe and shall be invoiced at the unit price as shown on the bid sheet. The submitted price shall include both the installation and removal of the plug.

    - Temporary plugs used to block the storm pipes for dewatering purposes shall be removed prior to rainfall events or at the determination of the County at no additional cost.  The Contractor shall be held accountable for any and all damages due to flooding caused by blocking of the storm drainpipe system if not removed in a timely manner.

    - When pumping and bypassing is required, the Contractor shall supply all equipment, labor, and supervision. The bypass system must be sufficient to handle expected storm flow plus any additional flow that may occur during a rainstorm.

    - If pumping is required on a twenty-four (24) hour basis, pumps should be equipped in a manner to keep noise to a minimum.

  - WATER JET CLEANING

    - Cleaning of the pipe, inlet box, box culvert, or water quality unit, shall be completed with the use of high-velocity jet (hydro-cleaning) equipment.

    - The equipment shall have a minimum capacity of fifty (50) gallons per minute and a working pressure of two thousand (2,000) pounds per square inch.

    - The nozzles shall be capable of producing a scouring action from fifteen degrees (15°) to forty-five degrees (45°) in all size lines designated to be cleaned.

    - All high-velocity cleaning equipment shall be constructed for ease and safety of operation.

    - There shall also be available a high-velocity gun for washing and scouring manhole walls and floor.  The gun shall be capable of producing flows from fine spray to a solid stream.

  - ROOT TREATMENTS

    - Roots shall be removed from the designated sections where root intrusion is a problem.  Special attention should be used during the cleaning operation to ensure complete removal of roots from the joints.

    - Any roots which could prevent the proper application of chemical sealants shall be removed.

    - Procedures may include the use of mechanical equipment such as, but not limited to, rodding machines, bucket machines and winches using root cutters and porcupines, and equipment such as high-velocity jet cleaners.

    - If it is found that the process of removing the roots from the pipes is causing damage to the pipe, the operation shall be stopped, and the County shall be notified before further work commences.

  - CHEMICAL ROOT TREATMENT APPLICATIONS

    - Chemical root treatment may be used by the Contractor at the option of the County, with prior written approval for the type of herbicide and application procedure.

    - Chemical treatment shall not be applied without providing proof of chemical applicators licensure.

    - Chemicals shall include but are not limited to herbicides and shall be applied in accordance with the manufacturer’s instructions and applied to ensure public health and safety.

    - Contractor shall adhere to the State Board of Health and other local and federal regulations and is responsible for any damage caused by its spraying or broadcasting.

    - The application of herbicide to the roots shall be done in accordance with the manufacturer’s recommendations and specifications and it shall be applied in such a manner to prevent damage to surrounding vegetation, which could also include vegetation that may exist in a surrounding body of water.

    - Any damaged vegetation designated by the County shall be replaced by the Contractor at no additional cost.

    - All Safety Data Sheets (SDS) for all chemicals used, including fuel used in any equipment, shall be supplied to the County.

  - COLOR VIDEO INSPECTIONS

    - Equipment required to perform video recording shall have a lens capable of rotating three hundred and sixty degrees (360°), capable of operation in 100% humidity while producing clear, color video recordings to the County’s satisfaction. If the video quality is deemed unsatisfactory, no payment will be made for that portion of work.

    - Video operations shall commence after the cleaning, and all water flow must be stopped during the video process so the entire pipe including the bottom portion will show in the recording.

    - Contractor shall furnish to the County a copy of all video inspections of the storm drains at rates of no greater than thirty (30) feet per minute, unless otherwise designated.

    - The color video shall include a narrative stating the location and an explanation of deficiencies such as cracks, leaks, failed patches, intrusions, subsidence, stains and any other anomalies observed.

    - The quality of the video shall be such that all deficiencies are clear and visible.

    - If the camera will not pass through the entire drainpipe segment, an attempt from the opposite end is required.  If the camera fails to pass through the entire manhole section or drainpipe segment a second time, the task shall be considered complete, and no additional viewing will be required.

    - Contractor shall invoice the County at the per linear foot unit rate for the footage that was captured and detailed in the CCTV report.

  - WATER QUALITY UNITS

    - It shall be the responsibility of the Contractor to ensure that all units are properly cleaned as per the manufacturer’s specifications.

    - County will issue an annual inspection request for all units and cleaning will be requested based on the details of each inspection report.

    - Contractor shall have the ability and experience to assess the operational condition, structural integrity, and maintenance needs of each unit to ensure effective treatment of stormwater runoff.

    - It is the responsibility of the Contractor to ensure that the debris, including oils or other chemicals, removed from the unit are properly disposed of as required.

    - There are currently thirty-one (31) water quality units in Lake County.  A listing of the location and type of water quality units can be found as an attachment to this solicitation.

  - BOX CULVERTS

    - Contractor shall be responsible for ensuring that all structures are properly cleaned at the discretion of the County.

    - County will issue an annual inspection request for all structures and cleanings will be requested based on the details of each inspection report.

    - County anticipates cleaning each structure biannually or once every two years.  The quantity of services may increase or decrease depending on the amount of debris that has accumulated within the structure.

    - It is the responsibility of the Contractor to ensure that the debris removed from the culvert is property disposed of as required.

    - There are nineteen (19) structure locations in Lake County.  The Contractor shall invoice the County per cubic yard of spoils removed.  A listing of the locations can be found as an attachment to this solicitation.

- EMERGENCY RESPONSE

  - When emergency response is requested, the County will specify on the project order form.

  - Contractor shall mobilize and respond to emergency service requests within 24 hours of notification. All work shall be completed and the affected pipe(s) fully restored to operational condition within 48 hours of the initial service request, unless otherwise approved in writing by the County.

  - Services shall include, but are not limited to securing water access, debris and blockage removal, cleaning, and ensuring proper flow restoration. Contractor shall furnish all labor, equipment, materials, and incidentals necessary to perform the services in a safe and timely manner.

- DOCUMENTS AND REPORTS

  - Contractor shall provide the County with a detailed summary report of all work completed for each Project Order. Each report shall include the following:

    - The culvert size, length of the segment, sump depth within the inlet box, storm drainpipe inverts at each end, and type of storm drain.

    - An outline including the type and severity of each observed defect.

    - Field report copies to further assist the County in understanding and using the results of the project viewed.

    - An aerial map depicting the location of the storm drainpipe or inlet box, box culvert, or water quality unit shown.  Any deficiency detected from the video or observed during the cleaning process shall be indicated on the map with the footage of where the deficiency occurs.

    - Video, if requested, of the pipe.

    - GPS coordinates both ends of the pipe or box culvert.

  - This report shall be submitted to the County within ten (10) calendar days of completion of all field activities and within the stated time of completion for each project.

- BASIS OF PAYMENT

  - Contractor shall be compensated at the unit price, as specified in the Contractor’s bid proposal, multiplied by the actual units completed and accepted by the County, less any damages assessed.

  - Pricing submitted shall include all: labor, equipment, materials, fuel, maintenance of traffic, mobilization, debris removal and disposal, and all incidentals necessary to complete all work as specified.

  - Each Project Order Form issued to the Contractor will have estimated quantities.  If for any reason the estimated quantities are significantly different than the actual quantity, the Contractor shall notify the County of the discrepancy prior to the commencement of work.

  - Contractor shall provide to the County all field reports, video inspections, and debris removal tickets with or prior to submitting an invoice for payment.

[The remainder of this page intentionally left blank]