Office of Procurement Services

P.O. Box 7800 • 315 W. Main St., Suite 416 • Tavares, FL 32778

SOLICTATION: Commercial Tenant Improvements				03/12/2026

Vendors are responsible for the receiving and acknowledging all solicitation addenda. An electronically signed copy of each addendum must be submitted along with the solicitation response. Failure to acknowledge any addendum may result in the submission being disqualified from award consideration.

THIS ADDENDUM DOES NOT ALTER THE PROPOSAL SUBMISSION DEADLINE.

QUESTIONS/RESPONSES

- What form should be used in the place of a reference form?

Response: Attachment 4 – Similar Projects Form.

- On sheet E801 the feeder schedule does not meet the amperage of the panel or switchboard it is feeding. Please have EOR provide the correct feeder schedule. We may need to show that the feeders need to run in parallel. See below.

Can’t handle 1000A

Response: On the feeder schedule, The parenthesis indicates the number of parallel sets. For example, (3) 3#500kcmil,#500kcmil N, 4"C, means 3 sets of conductors. And each set is comprised of three 500kcmil (One for each phase), one 500kcmil for Neutral), all in a 4” conduit. When grounded, the ground size is designated as G. All conductors are CU unless specifically identified as AL.

- Mechanical drawings show the RTUs as existing but the electrical drawings don't specify if the wiring and disconnects should remain existing, be replaced with new or if we need to re-route the feeders. Please advise?

Response: All disconnects and feeders shall be new.

ADDITIONAL INFORMATION

- Exhibit H – Construction Drawings version 02.23.2026 are hereby removed from the solicitation documents and replaced with Exhibit H – Construction Drawings, version No. 3 Addendum.

ACKNOWLEDGEMENT

Firm Name:  Click or tap here to enter text.

I hereby certify that my electronic signature has the same legal effect as if made under oath; that I am an authorized representative of this vendor and/or empowered to execute this submittal on behalf of the vendor.

Signature of Legal Representative Submitting this Bid:  Click or tap here to enter text.

Date: Click or tap to enter a date.

Print Name: Click or tap here to enter text.

Title: Click or tap here to enter text.

Primary E-mail Address: Click or tap here to enter text.

Secondary E-mail Address: Click or tap here to enter text.