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Office of Procurement Services
P.O. Box 7800 • 315 W. Main St., Suite 416 • Tavares, FL 32778
SOLICTATION: Generator Replacement				08/20/2026

Vendors are responsible for receiving and acknowledging all solicitation addenda. A signed copy of each addendum must be included with the solicitation response. Failure to acknowledge any addendum may result in disqualification from award consideration.
THIS ADDENDUM DOES NOT ALTER THE PROPOSAL SUBMISSION DEADLINE.
QUESTIONS/RESPONSES
1. Please identify the location of the new transformer? 
Response: The generator should be installed outside, where allowable by code, close to the existing fuel tank and infrastructure. Refer to the aerial map named Exhibit I - Transit Generator Location.
2. Can the Automatic Transfer Switch (ATS) be placed outside if rated for outdoor use? 
Response: Utilize the existing ATS if possible. ATS should remain indoors.
3. What fuel source is preferred? Fuel type shall remain propane. 
Response: Design to utilize the existing propane tank/source.
4. How big is the propane tank on site, if that is the preferred fuel source? 
Response: The underground fuel tank size is unknown.
5. Does the unit need to be fenced in? And if so, what type of fence should we include? 
Response: Yes. Match the existing chain link fencing at the facility.
6. Are there any future loads that we should account for when sizing? 
Response: Generator shall be designed to service existing infrastructure loads plus 25% for future needs.
7. Is the intent to swap like-for-like generators or increase the size? If an increase is desired, please list the additional loads you wish to have backed up. 
Response: The new generator shall back up the entire service for the building plus 25% for future expansion.
8. Can you provide 12 months of power bills for this site to assist in sizing the generator? 
Response: Utility bills power consumption data is provided below:
	Month
	Power Consumption KWH


	August 2025
	3058

	September 2025
	2817

	October 2025
	2482

	November 2025
	1403

	December 2025
	1319

	January 2026
	1619

	February 2026
	2996

	March 2026
	1542

	April 2026
	1591

	May 2026
	2153

	June 2026
	2847

	July 2026
	3622



9. Please verify the new unit is to be placed outside the building as discussed on site and if the County has a preferred location? 
Response: Yes. The new generator shall be installed outside. Please see the map of the proposed location in Exhibit I – Transit Generator Location.
10. Please verify if the existing underground LP fuel tank is to be removed or re-used. 
Response: Reuse existing propane tank if possible.
11. If the existing LP fuel tank is not being reused, please verify the type of fuel the County wants for the new generator and the desired runtime. 
Response: Fuel source to remain propane. Desired runtime should be 24 hours.
12. Will temporary power be required for this project and how long can the facility be without power? 
Response: Contractor to develop a detailed outage/cutover plan and coordinate it with the County project manager. Facility should be without power for a minimal amount of time. For Final utility/generator cutover, 2-4 hours.
13. Should work be done during normal business hours, or is weekend work preferred? If work is done on a weekend, is temporary power still required? 
Response: Work can be performed during normal business hours.
14. What should be done with the old equipment that is to be removed? 
Response: Removed equipment to be disposed of in a legal and proper manner by the Contractor.
15. Are we backing up the entire complex? 
Response: Yes. The generator shall be designed to service existing infrastructure loads plus 25% for future needs. 
16. I know at this time there is a 12kW, 120/240v, 1ph, NG generator located in the electrical room. Are we putting back into the room? 
Response: The generator should be installed outside, where allowable by code, close to the existing fuel tank and infrastructure. Refer to attached aerial map named “Transit generator location”.
17. What is the generator currently backing up? 
Response: Unknown. Minimal back up currently.
18. Are we replacing the Eaton ATS as well? 
Response: Utilize the existing ATS if possible. ATS should remain indoors.
ADDITIONAL INFORMATION
Exhibit I – Transit Generator Location, Exhibit J – Generator Project Photos, and Exhibit K – Generator Application Checklist are hereby added to the solicitation documents. 

ACKNOWLEDGEMENT

Firm Name:  Click or tap here to enter text.
I certify my electronic signature carries the same legal effect as a signature made under oath and I am an authorized representative, with full authority to execute this submission on the vendor’s behalf.
Signature of Legal Representative Submitting this Bid:  Click or tap here to enter text.
Date: Click or tap to enter a date.
Print Name: Click or tap here to enter text.
Title: Click or tap here to enter text.
E-mail Address: Click or tap here to enter text.
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