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Office of Procurement Services
P.O. Box 7800 • 315 W. Main St., Suite 416 • Tavares, FL 32778
SOLICTATION: Generator Repair and Maintenance 				08/13/2026

Vendors are responsible for receiving and acknowledging all solicitation addenda. A signed copy of each addendum must be included with the solicitation response. Failure to acknowledge any addendum may result in disqualification from award consideration.
THIS ADDENDUM DOES NOT ALTER THE PROPOSAL SUBMISSION DEADLINE.
QUESTIONS/RESPONSES
1. Will load-bank testing be scheduled during normal work hours?
Response: Load bank testing will be conducted during business hours. The Detection Center and Prelude will have to be done between 7:00 AM - 3:30 PM (EST).
2. Are there any location factors such as rooftops, parking garages, etc. that may affect any given service?
Response: There are several locations that the company will need to contact the County for access. For example, the equipment located at the Detention Center, Prelude, ECOC, SAB, 1975 Plant and the 1990 Plant is behind secured fences or inside buildings.
3. Can Lake County provide a detailed scope of work in regard to the expectations of the generator inspections, both annually and semi-annually?
Response: See Exhibit A - Scope of Work
4. Will the County perform fluid and filter changes in house, or will the contractor be responsible for this scope of work?
Response: The contractor will be responsible for all electrical portions of the generator. The County will be responsible for performing all maintenance and repairs to the engine of the generator.
5. The scope of work listed for the ATS inspection would require them to be de-energized. Can the County confirm that they are willing to de-energize each site for this period of time?
Response: The County requires that all Automatic Transfer Switch inspections and maintenance be performed without de-energizing or interrupting power to the facility. The Contractor shall utilize bypass-isolation procedures, or equivalent methods, to perform the required inspection, testing, and maintenance tasks while the switch remains in service. If any specific ATS unit does not have bypass-isolation capability, Contractor shall notify the County in advance so that scheduling and risk mitigation can be addressed on a case-by-case basis.
6. Will the County accept digital inspection reports and documents in place of paper copies for the requested logbook?
Response: See section 2.11.1 of Exhibit A – Scope of Work
7. The Annual states “Inspections”. Normally this would include semiannual inspections + fluid and filter changes, and most case at least a fuel sample. It states per NFPA 110 which just covers the load banking, startup, load, and cooldown times and temps. Does the county just want inspections and load banks during the annual and complete the fluid and filter changes per the recommended hours for each engine? Fuel samples are upon request.
Response: The Annual Inspection is outlined in section 2.6 of the Scope of Work.  

ACKNOWLEDGEMENT

Firm Name:  Click or tap here to enter text.
I hereby certify that my electronic signature has the same legal effect as if made under oath; that I am an authorized representative of this vendor and/or empowered to execute this submittal on behalf of the vendor.  
Signature of Legal Representative Submitting this Bid:  Click or tap here to enter text.
Date: Click or tap to enter a date.
Print Name: Click or tap here to enter text.
Title: Click or tap here to enter text.
Primary E-mail Address: Click or tap here to enter text.
Secondary E-mail Address: Click or tap here to enter text.
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