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Office of Procurement Services
P.O. Box 7800 • 315 W. Main St., Suite 416 • Tavares, FL 32778
SOLICTATION: Construction of LCSO Marine Facility and Existing Pole Barn Expansion 09/04/2026

Vendors are responsible for the receipt and acknowledgement of all solicitation addenda. Submit an electronically signed copy with solicitation submission. Failure to acknowledge an addendum may prevent the submission from being considered for award.
THIS ADDENDUM CHANGES THE SUBMISSION DEADLINE FROM THURSDAY, SEPTEMBER 17, 2026 (09/17/2026) TO THURSDAY, SEPTEMBER 24, 2026 (09/24/2026 – 3PM EASTERN.
ADDITIONAL INFORMATION
E.	To eliminate potential confusion regarding individual sheet revisions, a fully integrated, consolidated set incorporating all revised sheets into the complete plan set has been issued by the design consultant. This final, combined drawing set supersedes and replaces all previously published construction drawings in its entirety. 
Bidders shall base their bids and proposals strictly on this consolidated set, as it represents the official, current, and governing technical construction documents for this solicitation. 
All previously published exhibits that are not construction plans are still in effect and have not been replaced or revised.
	All Contractors that have submitted Attachment 5 may view the complete set of plans at the link previously provided. See folder labeled “Plans – Final”.
QUESTIONS/RESPONSES
76.	Please confirm whether an Edwards fire alarm system will be accepted as an approved equal substitution under Specifications Section 28 31 11, or if the Contractor is required to furnish one of the five named manufacturers specified in the contract documents?
A. See response to Question #70
77. Please confirm if Fire-Lite or Silent Knight would be an accepted as an approved equal?
A. Lite or Silent Knight would be an acceptable equal to manufacturers listed on sheet E0.4.
78. Was the pre-proposal meeting mandatory?
A. No.
79. Per Exhibit P for the temp fence, do the wood poles need to be square or round as shown in the pictures? Is chain link acceptable?
A. Wooden poles can be square or round.  Chain link would be acceptable if the height and general opacity are in accordance with Exhibit P but the cost of chain link that tall is typically prohibitive.  The County has had far more success with the wooden posts and screen as the most economical alternative.   
80. For the toilet accessories, will you accept ASI accessories?
A. No, please provide Bobrick.
81. Room 116 wall tile above prefab shower unit. The finish schedule reads "porcelain tile wainscot to 48" ht. at non-wet walls, full height at wet walls & showers." Room 116's shower is a prefabricated unit (SH-1, Aquatic 6030BFSC) with its own integral surround up to the unit's rim/flange, so there's no wall tile inside the unit itself. Please confirm: (a) is tile required on the wall above the prefab unit's flange up to the ceiling, or does the prefab surround satisfy the "full height at showers" note on its own? and (b) are the remaining wet walls in 116 (lav/WC walls) full height or 48"? This is roughly an 80 SF vs. 200+ SF swing in wall tile.
A. Tile is not required above the prefabricated shower unit. b) Wet wall with Lavatory and Water Closet are to be full height wall tile (per “Remarks” in the Finish Schedule for room 116 on sheet A10.4), all other walls inside room 116 shall be tile up to a 48 inch high wainscot note (per “Remarks” in the Finish Schedule for room 116 on sheet A10.4) and notes on details 7 and 9 on sheet A10.1
82. Product designation consistency (Section 096200). Section 096200, titled "Luxury Vinyl Tile," specifies Tarkett iD Latitude Wood Series in 6" x 48" plank format. The finish schedule tags this material as "LVP." Please confirm both references are intended to designate the same product, so there's no discrepancy in the bid documents.
A. We do not have ‘LVP’ designation. We do call out LVT1 on sheet A10.4 Finish Legend that is referenced in spec section 096200 for the 6 x 48 iD Lattitude Wood Series Resilient LVT.
83. Epoxy floor system and cove base height (Section 096710). The spec's Floor System paragraph (§2.3.C) lists two separate primer/cove-base packages back to back - one using 3579 primer, one using GP 3561V primer with GP 5113 additive - without indicating which applies to which room. Please confirm which package governs for Rooms 114, 115, and 117. Separately, please confirm integral floor cove base height for these rooms: §2.3.C states 6" for the first package, while §2.3.G.1 directs to "height as indicated on the Finish Schedule" - that schedule table isn't legible at the resolution of our plan set, so we're unable to confirm independently.
A.  The spec section 096710.2.3.C is a generic specification. Please provide a 6 inch high base as mentioned in the specs. Basis of design product is to be per sheet A10.4 Finishes Legend, EP1: EPOXY FLOOR SYSTEM IS INCLUDED AS DEX-O-TEX CHEMINERT HD (APPROX. 1/8TH OF AN INCH THICK.). Provide all components as required for a complete system. All components will be the same for the floor and base inside of rooms 114, 115 and 117.
84. Epoxy wall wainscot. Section 096710 references a 4' high wall wainscot application with 4" cove base at typical condition. Please confirm whether any epoxy wall wainscot is scheduled on this project and, if so, in which locations.
A. This project does not require the 4 foot high wainscot as part of the EP1 Epoxy Floor System – please delete spec reference 096710.2.3.D in it’s entirety.
85. Rubber base height (Section 096513). The spec states height "as indicated on Drawings," but neither the drawings nor the finish schedule specify 4" vs. 6". Please confirm.
A. Please see sheet A10.4, Finishes Legend, Base Finishes, V2, mentions 4 inch rubber cove base.
86. Mop sink wainscot location. MS-1 appears in Room 110 (Mech./Elec.) per Sheet P3.1. Please confirm the 48" porcelain wainscot at the mop sink is located in Room 110, and identify which wall(s).
A. Refer to detail 4/A10.4, elevation ‘G’ which mentions Tile over Gyp. To 48” A.F.F., add the following “(Typ. of 3 walls bordering mop sink)”.
87. Sealed concrete (approx. 87 SF). This scope appears only in Section 09900 (Painting), with no corresponding section under Division 09 Flooring. Please confirm this is Painting's scope rather than Flooring's.
A. Per sheet A10.4 Finish Schedule, please provide “Sealed Concrete” finish in rooms 110, Covered Entry (exteriors) and Covered Patio (exteriors). Provide per spec section 099000.3.06.7 Concrete Floor (Sealer) – Sealed Concrete.
88. Epoxy manufacturer conflict. The drawing legend (EP1) calls out Dex-O-Tex Cheminert HD, while the Section 096710 spec body is written around Key Resin product codes (3579, 3746, 6750/6755, 4638, EPO-FLEX). Please confirm the basis-of-design manufacturer so all bidders are pricing the same system.
A. See Response to question #83.
89. Wainscot cove base condition. Where porcelain wainscot terminates at the floor, please confirm whether a Schluter cove profile is acceptable as an alternate to porcelain cove base, or whether porcelain cove base is required in all locations. (This is distinct from the Schluter cap-as-alternate at the top of the wainscot, which is already addressed per Spec §2.3.A.1.a.4 — this question is specifically about the floor-to-wall junction under §2.3.B.5.)

A. Refer to spec section 09310.2.3.2.a and provide Schluter transition for floor tile to wall tile base.
90. Exhibit I is calling for a Berridge “Tee” Panel in .032 aluminum with 2" rib height to be installed on the roof of the Technical Facility.   Berridge does not have a Florida product approval code for the Tee panel in aluminum, so we cannot technically install this panel. The  Tee panel also does not have a 2" rib height. The closest option in aluminum would be a Berridge "Cee" panel which is a continuous clip system and a 1.5" rib height and the "Double ZEE Lok" panel which is a mechanically seamed panel with a 2" rib height.
A. Please refer to both Marine Facility and Pole Barn spec sections 07610 Metal Roofing, subsection 2.1.A.1, revise to read: “Panel Designation: Double-Lock Zee-Lock Panel, with Floating Zee-Clip”. In subsection 2.1.B.1 and 2 as well as C.1, revise to read “Panel Designation: Comparable to Basis of Design”. In addition, refer to sheet A7.1 on both projects, Roof Plan General Notes, revise existing note #3 deleting references to metal roof or “R” Panel Metal roof by adding the following at the end of note #3: “Roof Panel Basis of design: Berridge Manufacturing Co., Double-Lock Zee-Lock Panel, with Floating Zee-Clip, Florida Product Approval # FL 19999.1 R5. ACCEPTABLE MANUFACTURER: Innovation Metals Company (IMETCO), and ASC Building Products.”
91. A subcontract notified us that, regarding the specified metal panel systems, they do not offer a wall-to-wall (WTW) exposed fastener wall panel matching the specified application Please clarify how you would like us to proceed.
A. See Response to question #93.
92. A subcontractor notified us that they do not have Florida Product Approval for the specified .032 aluminum wall panels. Please clarify how you would like us to proceed.
A. See Response to question #93.
93. Is the specified Berridge "M" Panel for the wall assembly still required, despite the manufacturer advising it is not available as specified? 
A. Please refer to Pole Barn spec sections 074213.13 Formed Metal Wall Panels, subsection 2.1.A, revise to read: BASIS OF DESIGN: Metal Sales Manufacturing Co., 7800 Highway 60, Sellersburg, IN 47172, (800) 406-7387. In subsection 2.1.A.1, revise to read “Panel Designation: 26 GA. Min. R-Panel, Corrosion resistant, PVDF Kynar finish”. In subsection 2.1.B.1 as well as C.1, revise to read “Panel Designation: Comparable to Basis of Design”. In the spec section, revise all references from 0.032” Aluminum wall panels to “Corrosion resistant, Min. 26 ga., 80 ksi steel or min. 24 ga., 50 ksi steel.” In addition, refer to Pole Barn sheet A3.2A, Floor Plan General Notes, add new note #7: “Formed Metal Wall Panel Basis of design: Metal Sales Manufacturing Co., 26 GA. Min. R-Panel, Corrosion resistant, PVDF Kynar finish, Florida Product Approval # FL 46539.3. ACCEPTABLE MANUFACTURER: Innovation Metals Company (IMETCO), and ASC Building Products.”
94. Is the specified 0.032 aluminum wall panel still required even though Berridge does not have a Florida Product Approval for this product?
A. See Response to question #93.
95. Will you accept Berridge’s 24-guage Galvalume steel panel with Florida Product Approval as an approved substitution? If not, please identify the acceptable manufacturer and product that meets both the project specifications and the required Florida Product Approval.
A. No. See response to question #90.
96. On sheets 4.1, 4.2, 4.3 respectfully, in the elevation notes #6 calls for “Woodgrain finished tongue and groove aluminum cladding.” Can you provide manufacturer and specifications on this product requested.
A. Please see response to question #42.
97.  The construction documents specify a specific security system under the low voltage scope of work. Please clarify whether this system is to be furnished and installed by the owner-vendor, owner-subcontractor, or if the General Contractor (GC) is required to carry the complete costs in the base bid.
A. Verkada Equipment and Operating Systems will be furnished by Owner and installed by Contractor.  All low voltage cable and specified termination connections will be furnished and installed by the awarded contractor in preparation for the system installation. Refer to the responsibility matrix on sheet T6.1 of the construction plans Section 6 – Security Systems, Number 6.3 stating that active electronics such as cameras, DVR’s and controls are to be owner provided. 
98.  The construction documents calls out a specific security system for the Access Control System under the Low Voltage scope. Please confirm whether the supply and installation of this equipment will be performed by the owner-selected subcontractor or if the GC must include full procurement and installation costs in the base bid.
A. See answer to Question 97.  
99. Please clarify which party is responsible for carrying the cost to furnish and install the televisions and TV mounting brackets for this project, and if the scope calls under the GC’s base bid, please provide detailed specifications including the make, model, quantity, and display size for each location.
A. Contractor will furnish and install televisions, mounting brackets and, all cabling, access panels, and accessories as described in the construction plans on sheet T6.1 under the “Electrical Technology Special Outlet Schedule”.  This schedule contains make, model, and display size.  Sheet T2.1 specifies the specific locations and counts of the TV’s.  The Design and Construction Responsibilities Table on Sheet T6.1 Section 4.04 should revise to indicate the Procurement Responsibility as “GC”. 
100. Please clarify responsibility for the supply, installation, and termination of all low voltage cabling/wiring. Kindly confirm if all low-voltage wiring is to be carried within the GC’s base bid scope, or if any portion is designated as owner-furnished / owner-installed.
A. All low voltage cabling and specified termination connections are to be procured and installed by the contractor.  See the responsibility matrix on Sheet T6.1 of the construction documents for the LCSO Marine Building. 
101. Please clarify the required scope of painting for the pole bar. Specifically, does the pole barn receive pain finishes? If yes, should painting costs be carried solely for the new structural additional, or is the contractor required to repaint the existing structure as well to match. Please provide clear scope limits/elevations.
A. There is no paint or finish schedule for the pole barn.  Either through the newly constructed side or any refurbishing of the existing side.
102. The manufacturer calls out in the specs do not offer an NDL warranty on their exposed fasteners nor do they have Florida Product approvals on M and R panel for aluminum in Florida. Please advise how we should proceed.
A. Please see response to question #91.
103. On the drawings there is a new flagpole to be installed. Please advise on its specifications.
A. Please refer to question #23 response.
104. For the fire alarm system, will Silent Knight be an approved alternative?
A. Please refer to question #77 response.
105. Please indicate sizes of handrails in Hallways 100D and 100F.
A. Please refer to detail 2/A10.1 which has note saying: 1-1/2 INCH ROUND WOOD HANDRAILS WITH TOP @ 36" A.F.F. (TYP. ON BOTH SIDES OF RAMP). PROVIDE 12" EXTENSIONS RETURNED TO WALLS
106. With storefront spec, Kawneer is the BOD, but YKK threshold is mentioned. Can YKK be an acceptable manufacturer?
A. Please refer to question #70 response. YKK has been added as an acceptable manufacturer.
107. Please confirm appliances by owner.
A. Owner will procure and install the appliances.  Awarded contractor will be responsible for procuring and installing proper functioning connections for those appliances by substantial completion.
108. Please provide a detail and spec for flag poles. Are bases to be concrete?
A. Please refer to question #23 response, base is concrete and to be provided by the Contractor (including calculations by a Florida P.E.).
109. For the pole barn, provide a dimensional floor plan based on structural, and not pole locations. Current plan set has all dimensions to the center of poles.
A. Refer to the Architectural Floor plan shown on sheet A3.2A and sheet S1.4 respectively, both Architectural and Structural dimensions match and are supplementary of each other.
110. Please provide a list of approved manufacturers for the Low Voltage, Fire Alarm, CCTV, Access Control, and Audio-Visual Systems.
A. See Exhibit A’s, Section 6.
111. Will any of the technology systems (Access Control, CCTV, or Fire Alarm) be integrated with the existing facility systems? If so, please provide the integration requirements.
A. The PACS & VSS (CCTV) will be by Verkada as directed by Owner. Contractor shall provide & install all PACS & VSS cabling and equipment as shown on contract documents. These systems will be connected to the Owner’s Verkada platform via internet connections. No integration required by contractor. The fire alarm system is a stand-alone system with no integration required, only monitoring by Owner’s central monitoring station.
112. Question 6 references Exhibit Q – Sheriff’s Logo, however there is no Exhibit Q in the solicitation documents.
A. See full bid documents at link previously provided.
113. Please confirm there is no painting cope at the barn.
A. Refer to answer to Question 101 of this addendum.
114. Please specify if wood doors require painting or are factory finished.
A. Refer to question #54 response, factory finish per spec section with stain to match (PL1) P-Lam color as per note ‘S1’ on sheet A10.4.
115. The east elevation where the “Lake County Sheriff’s Office” is located calls it out as M-1 exterior finish (Nichiha, fiber cement board); and building section 2 on A5.8 calls it out as “Woodgrain Finish Tongue & Groove Aluminum Cladding”. Please advise which finish is correct.
A. See response to question #42.
116. The west elevation shows the batten board (S-1) going over door 100B. Please advise if this is correct. If so, please further details on how it will be attached.
A. This will be cleaned up so that ‘S-1’ board batten does not conflict with the door; additional details are not required.
117. Please confirm that Innovation Metals Company (IMETCO) & ASC Building Products are acceptable substitution for the metal roofing per the metal roofing spec.
A. Please note that for both projects, spec section 07610, subsection 2.1, B and C are already calling out that Innovation Metals Company (IMETCO) & ASC Building Products are acceptable substitutions manufactures.
118. Please provide structural wall detail for the 2x6 stud wall.
A. Refer to question #50 response.
119. Plumbing drawing do not call out for or schedule a hot water circulation pump on their plans but if you refer to the electrical panel schedule on drawings E6.3 panel PB call out for wiring of a RCP-1. It is also referred to on the mechanical equipment wiring schedule on E6.2.. Is a recirculation pump required on this project?
A. A recirculation pump will not be required for this project. Contractor shall remove “RCP-1” from panel PB on sheet E6.2 and replace with “Spare” circuit breaker.
120. Drawings E6.1 electrical one line diagram shows a 60 amp breaker and feeder from MDP panel to AC-1 however, if you refer to HVAC drawing M0.1 AC-1 is not schedule or shown on the Mechanical drawings. Please confirm if there is a AC-1 included and provide specifications and location of AC-1 on the Mechanical drawings.
A. AC-1 as referred to on the One-Line on sheet E6.1 is designated for Owner provided Air Compressor as shown on sheet E2.2 below Equipment Storage & Servicing 117 on the exterior of the building.
121. On the blueprints (Sheet A8.1), the door appears to be essentially all glass. However, Specification Section 083613, calls for Overhead Door Corporation, model ThermaCore 515, which is an insulated galvanized steel door. We need to confirm which is correct. The glazed appearance shown on the drawings, or the steel door in the specifications.
A. Refer to question #33 response.
122. The contract documents confirm that permits, licenses, and inspection fees are the Contractor’s responsibility. However, they do not address impact fees. We need to confirm whether utility impact fees are included in the Contractor’s scope or will be paid directly by the Owner.
A. Impact fees will be covered by Owner
123. Exhibit O, Sample Agreement, Section 7.35 states that this project is subject to prevailing wage. Florida does not have a states prevailing wage law, so this requirement would only apply if the project were a Davis-Bacon / federally funded project. We need to confirm whether this is a Davis-Bacon project with a formal wage determination and certified payroll requirement.
A. Federal Funding will not be used for this project.
124. The Technology Systems drawing reference a Responsibility Matrix for details on which equipment is Owner-furnished versus Contractor-furnished, but the matrix is not included in the bid set. We need to confirm and obtain the Responsibility Matrix so we can correctly identify what is in our scope and avoid duplicated or omitted pricing.
A. The Responsibility Matrix is located on Sheet T6.1 of the Construction Documents for the Marine Building.
125. Specification Section 083613 for Door Type G2 addresses air infiltration but does not mention water infiltration. We need to confirm whether Door Type G2 requires water infiltration resistance testing (ASTM E331 / E547).
A. Yes. Please refer to sheet A8.1 (Door) ‘General Notes’ and sheet A8.2 ‘Aluminum Storefront Notes’; add the following: “H. EXTERIOR FIXED WINDOWS, EXTERIOR ENTRANCES AND EXTERIOR DOORS SHALL MEET WATER PENETRATION (ASTM E331) PERFORMANCE REQUIREMENTS (NO WATER LEAKAGE OBSERVED INTO THE BUILDING).”
126. Will this be a Davis Bacon project?
A. Federal Funding will not be used for this project. 
127. Will there be an ODP on this project?
A. Refer to responses to question #’s: 16, 17, 19, 20, 21, 23, 25, 26, 27, 28, 37, 38, 66, 67, 97, 98, 99, 100, 107, 148
128. Specifications Section 122413 states a Single Manual Roller Shades but mentions 5% and 0% Openness Factors. Can you please let me know what goes where because the plans do not say.
A. Refer to question #37 response.
129. Where will the staging area be on property for materials, dumpsters, portable toilets, etc.?
A. The staging area will be on site.  The staging area itself will be coordinated with the awarded contractor before or at the preconstruction meeting.  There are too many variables to specify the full area ahead of time as different contractors have different methodologies/preferences for staging, material storage, and logistical needs.   
130. Ceiling details 3 and 4 on Sheet A3.3 show sound batts above the acoustical ceiling time (ACT) grid. However, no sound batts are shown in the wall sections or building sections. Given that the basis of design is Armstrong 1911 Ultima tile, can you please clarify if insulation is required above the ceilings, and if so, to what extent?
A. Please refer to sheet A3.3, see detail 2/A3.3 Ledge detail, provide at vertical and horizontal gyp. Bd. As shown on that detail. Also refer to A3.3 “Reflected Ceiling General Notes”, Note number 4 which is calling out sound batts above gyp. board ceilings for the room numbers listed in note 4. In addition, refer to A3.3, “Reflected Ceiling General Notes”, Note number 1, revise note to read: 2 x 2 ACT CILING (PROVIDE SOUND ATTENUATION BATTS TYP. ABOVE CLG. IN 101, 102, 103, 104, 105, 106 & 112),
131. What is the projected project start date?
A. Refer to Question #60 response.
132. Provide Wall Types schedule for this project.
A. For Wall Type Tags, please refer to sheet A3.2, Floor Plan General Notes, see note #5 describing the typical wall designation. For any other wall than the typical, refer to A3.2 floor plan showing wall type tags. Then refer to sheet A6.1 for the wall type details to be used on this project.
133. The civil and structural drawings reference foundation and site work; however, a geotechnical report was not included in the bid documents. Please provide the geotechnical report, including recommendations for bearing capacity, groundwater elevations, unsuitable soils, undercut requirements, and compaction requirements.
A. Please refer to question #40 response.
134. Please clarify tree protection requirements, root protection zones, arborist inspections, and responsibility for any tree damage during construction.
A. See Sheet L-501 for the Tree Protection detail. The Demo Note number 4 on Sheet C101 Demolition Notes address the requirement of tree protection, and Sheet C600 also contains a Tree Protection Barricade Detail. Sheet C102 depicts the existing trees within work zone required to be protected. Also, arborist inspections are not specified by the construction documents, and we are not aware of any County Code requirements for arborist inspections.
135. Please provide details for exterior monument signage, building lettering, Sheriff’s graphics, and wayfinding signage.
A. For Exterior Signage, please refer to sheet A4.1, detail 2 East Elevation showing Badge Logo (keynote 5), building Address (Keynote 20), Lake County Sherrif’s Office lettering (keynote 7. For the Exterior Memorial Wall Signage, please refer to sheet A4.3 details 1 and 2 being revised per response to question #5. For interior room identification signage, refer to response to question #39.
136. Please confirm if storage sheds are to be included in the proposal.
A. Storage Sheds were completed by owner prior to this bid.  Storage sheds were included under recommendation of Lake County Planning and Zoning to combine all site plan modifications into one application.  The “Proposed Storage Sheds” to the north as identified in the Civil Site Plan drawings are not part of this project’s Scope of Work.
137. Please confirm whether an emergency generator or future generator connection are to be included in the proposal.
A. Contractor shall provide an emergency generator and associated generator docking station as specifically described on sheet E6.1. Generator and docking station shall meet all requirements of contract documents.
138. Please clarify responsibility for extending Owner fiber, communications backbone, and Sheriff’s network into the building.
A. Contractor will be responsible for pulling existing fiber into the new building.  Approx. 300ft of ready-to-pull fiber optic line is inside the vault box identified in the construction documents.  Connections and testing of connections will be the responsibility of the contractor.  The fiber should be pulled and terminated by the contractor in preparation for the LCSO installing their own equipment upon substantial completion. 
139. Please clarify whether utility company fees, transformer upgrades, and permanent service charges are included by the Contractor or paid directly by the Owner.
A. These fees/costs will be covered by owner. However, the contractor will be responsible for coordinating all service requirements, existing connections, new connections, upgrades, inspections, energizations schedule, and any other related need for the proposed electrical service system.  
140. Will a complete specification manual be provided for every scope of work? We noticed that all divisions after 12 are missing for the Marine Facility, and divisions after 10 for the Pole Barn Expansion.
A. The issued specifications manual address Architectural discipline, all other disciplines have listed their related specifications in their drawings. No other specification sections will be added to the Specifications Manual.
141. Structural Note 042201 on Sheet S0.3 indicates that a Temporary Wall Bracing Plan shall be prepared by a licensed engineer, shop drawings shall be submitted, and a specialty bracing engineer shall perform site observations during wall bracing installation and submit reports to both the Contractor and the Structural Engineer of Record. Please confirm whether these requirements will be mandatory for this project. Additionally, please advise whether an internally braced masonry wall system may be utilized in lieu of temporary exterior wall bracing. The proposed installation method would consist of constructing the masonry using a low-lift grout system, with vertical cells grouted in lifts not exceeding five (5) feet, in accordance with applicable code and industry standards.
A. The wall bracing plan is required for this project. Internally braced wall may be utilized.
142. Please provide the riser diagram for all electrical work included at the Marine Facility.
A. Contractor shall bid electrical work as shown on contract documents.
143. The elevation drawings make it appear that bathroom walls will also include a base as indicated in the drawings, however the finish schedule does not have it listed as receiving any. Please advise if the bathroom base will be bullnose, rubber base, or no base at all. Main concern comes from drawings indicating a 4” base height, when a bullnose is 3”.
A. For Interior Elevations on sheet A10.1, please disregard the 4 inch high wall base height shown. Please refer to spec section 09310.2.3.B calling out 3 inch high x 12 inch long base, and per item #3, provide a square edge at floor base (bullnose at top of wainscot).
144. Please provide the riser diagram for all electrical work included at the Marine Facility.
A. Please refer to question #142 response.
145. Is there transition detail drawings available to see the trim options shown under TS, and where they are planned to be installed. Please advise if transition detail drawings can be provided.
A. Transition details are not required. Please follow sheet A10.4 Finishes Legend, Transition Finishes, ‘TS1’ and ‘TS2’. In addition, please refer to spec section 09310.2.3.A.2 Tile Edge Transitions verbiage.
146. There was a mention of a T2 product, but I do not see one in the specifications or finish schedule. Please advise if this will be a newly added product or previously removed.
A. There is no T2 on this project. But assuming you are referencing to sheet A10.4 – Finishes Legend, Transition Finishes ‘TS2’, the reference to installing a transition needs to be revised to read “transition of T3 and T1 Tiles”.
147. The project is showing two different sized tiles to indicate wall tile. Please advise if this is just a cosmetic change, or if this should indicate a different material or pattern that must be followed for installation.
A. Assuming you are referencing to the interior elevations shown on sheet A10.1, as it is noted in those elevations – See Room Finish Schedule. Please refer to sheet A10.1’General Finish Notes’, notes ‘P’ & Q’, as well as the ‘Finishes Legend’ on the same sheet for Tile ‘T1’ and ‘T3’ Tile Base. In addition, please refer to spec section 09310.2.3, A and B for supplemental tile scope information.
148. Will the contractor be responsible for purchasing the American Flag to be flown? If so, what is the size? 
A. Owner will furnish and install flags
149. We did notice one conflicting/general note on the life-safety plan referencing a fire sprinkler contractor installing/modifying sprinkler. This appears inconsistent with the architectural code analysis identifying the building as non-sprinklered, so we are treating that note as something that should be clarified by the design team. 
A. Sprinkler system is not included in this construction project.  The building is designed and permitted as “non-sprinklered”.  Instances in which the sprinkler system is mentioned in the construction documents are only included as general notes for “if” a sprinkler system were to be integrated into the building.  

ADDITIONAL INFORMATION
The original manufacture (Great Lakes) of several items identified as contractor furnish and install (i.e. data racks, cabinets, and other related equipment) used as “Basis of Design” was purchased by a company known as “Vertiv”.  Due to the transition, some of the items previously called out in the construction documents as well as the technical specifications have new labels and SKU #’s.
To provide clarity to the vendors on the materials used as “Basis of Design” the below information contains the new labels and SKU #’s used by Vertiv:
Enclosed Rack in network room:
PROVIDE 45RU BLACK FLOOR MOUNTED DATA CABINET. RACK
Vertiv (Formerly GREAT LAKES) SKU: GL790ES-3048-B-MSS (NO SUBSTITUTIONS – CONFIRM CONFIGURATION AND REQUIRED ACCESSORIES WITH OWNER
PRIOR TO ORDERING). CABINET SHALL BE 84" HIGH BY 31.5" WIDE BY 47.25 DEEP WITH MSS CONFIGURATION. MOUNT RACK TO FLOOR PER MANUFACTURER'S RECOMMENDATION AFTER LOCATION HAS BEEN CONFIRMED WITH OWNER.
Ground isolation plates,
Vertical copper bus bar for grounding, model SKU: CBB-72
Vertiv GLC Casters Non-Locking SKU: 7208-ES
VERTIV 4SET ADJ 4IN LVLERS STEEL SIL SKU: 7209-4HD   
VERTIV-GLC ADJ LADDER RACK BRACKET SKU: LRBV4-8
2 post rack in network room:
Vertiv (Formerly Great Lakes) SKU: CMR-45U16-B-SQM6
PROVIDE (2) BLACK FRONT & REAR 8" WIDE BY 12" DEEP VERTICAL
CABLE MANAGEMENT (Vertiv (formerly Great Lakes) #VCM-45U-0812FR-B - NO
SUBSTITUTIONS). MOUNT RACK TO FLOOR PER MANUFACTURER'S
RECOMMENDATION AFTER LOCATION HAS BEEN CONFIRMED WITH OWNER.
2 PDU mounting bars from Vertiv SKU: VPCB1
Ground isolation plates from Vertiv, SKU: GL-ISOGLRR19
Vertical copper bus bar for grounding, model SKU: CBB-72
Outdoor NEMA box for pedestal to open garage door and Outdoor NEMA box for cameras on the pole barn:
SKU: BXSB04-24U42-GY-12-AC041-115
Manufacturer: Vertiv (formerly Great Lakes)
Link: https://racks.vertiv.com/product/nema-outdoor-cabinet/
Additional parts needed: https://racks.vertiv.com/product/wet-concrete-template/ (SKU: BXSBWCT42 - Single Bay and 42" Depth) Owner confirm that the 2" conduit that is ran from the building ends up in the right spot inside the NEMA box.

ACKNOWLEDGEMENT

Firm Name:  Click or tap here to enter text.
I hereby certify that my electronic signature has the same legal effect as if made under oath; that I am an authorized representative of this vendor and/or empowered to execute this submittal on behalf of the vendor.  
Signature of Legal Representative Submitting this Bid:  Click or tap here to enter text.
Date: Click or tap to enter a date.
Print Name: Click or tap here to enter text.
Title: Click or tap here to enter text.
Primary E-mail Address: Click or tap here to enter text.
Secondary E-mail Address: Click or tap here to enter text.
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